## Thickness
2025 | [30 empty] | OBSTRUCTION
|  | PLATENS NUMBERED LEFT TO RIGHT FACING REAR OF BOILER. THICKNESS MEASUREMENTS ARE IN INCHES. | [28 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | REAR SIDE | L | 1: 0.176; 2: 0.18; 3: 0.188; 6: 0.187; 9: 0.179; 12: 0.185; 15: 0.181; 18: 0.178; 19: 0.19; 20: 0.184 | 0.1828 | 0.176
0.075 | IK #22 C/L | C | 1: 0.176; 2: 0.182; 3: 0.189; 6: 0.183; 9: 0.179; 12: 0.184; 15: 0.181; 18: 0.178; 19: 0.186; 20: 0.186 | 5.3414 | 0.176
| 0' REFERENCE | R | 1: 0.176; 2: 0.182; 3: 0.189; 6: 0.185; 9: 0.179; 12: 0.185; 15: 0.181; 18: 0.179; 19: 0.19; 20: 0.186 | 7.0611 | 0.176
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | 0.001-0.075 | 0.146-0.155 | 10: OUTSIDE DIAMETER: |  |  | 2.5 | INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | INTERNATIONAL PAPER
LEGEND | 0.076-0.115 | 0.156-0.165 | 10: TUBE MATERIAL: |  |  | SA-213T22 | 0.19 | MAX. THICKNESS |  |  | RIVERDALE MILL
| 0.116-0.125 | 0.166-0.175 | 10: NOMINAL WALL: |  |  | 0.165 | 0.182 | AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY
| 0.126-0.135 | 0.176-0.185 | 10: ASME MIN: |  |  | 0.075 | 0.176 | MIN. THICKNESS |  |  | NO. 1 RECOVERY BOILER
| 0.136-0.145 | 0.186-0.999 | 10: MILL FLAG: |  |  | 0.115 | 0.0042943 | STD DEV. | Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  | 10 SOOTBLOWER PASS A1
THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Corrosion
2025 | [28 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. CORROSION RATE MEASUREMENTS ARE IN MILS. | [26 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MAX
A | REAR SIDE | L | 0.132 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.272 | 0.412
| IK #22 C/L | C | [20 empty] | 10.0196 | 20 | bar: 1 to 20
| 0' REFERENCE | R | ND | ND | ND | ND | ND | ND | ND | ND | 0.412 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 10.0196 | 20
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MAX
| CORROSION RATE (mpy): |  | 10: NOTE: CORROSION RATES ARE BASED ON COMPARISON OF |  |  | TEST RESULTS |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | INTERNATIONAL PAPER
LEGEND | < 0 mpy (LOSS) or no data | [23 empty] | OVERALL CORROSION RATE (mils per year): |  |  | RIVERDALE MILL
| 0-10 mpy (LOSS) |  | 10: 2020, 2023, 2024, 2025 | [5 empty] | CALCULATED CORROSION RATE
| 10-20 mpy (LOSS) |  | 10: INSPECTION DATA |  |  | 0.272 |  |  | NO. 1 RECOVERY BOILER
| > 20 mpy (LOSS) |  | 10: ND; 15: NO COMPARISON DATA |  |  |  | Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  | 10 SOOTBLOWER PASS A1
CORROSION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Projection
2025 | [30 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. PROJECTED THICKNESS MEASUREMENTS ARE IN INCHES. | [28 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | REAR SIDE | L | 1: 0.173; 2: 0.18; 3: 0.188; 6: 0.187; 9: 0.179; 12: 0.185; 15: 0.181; 18: 0.178; 19: 0.19; 20: 0.184 | 0.1825 | 0.173
0.075 | IK #22 C/L | C | 1: 0.176; 2: 0.182; 3: 0.189; 6: 0.183; 9: 0.179; 12: 0.184; 15: 0.181; 18: 0.178; 19: 0.186; 20: 0.186 | 5.3413 | 0.173
| 0' REFERENCE | R | 1: 0.176; 2: 0.182; 3: 0.189; 6: 0.185; 9: 0.173; 12: 0.185; 15: 0.181; 18: 0.179; 19: 0.19; 20: 0.186 | 7.0609 | 0.173
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | 0.001-0.075 | 0.146-0.155 | 10: OUTSIDE DIAMETER: |  |  | 2.5 | FUTURE PROJECTION |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | INTERNATIONAL PAPER
LEGEND | 0.076-0.115 | 0.156-0.165 | 10: TUBE MATERIAL: |  |  | SA-213T22 | 0.19 | MAX. THICKNESS |  |  | RIVERDALE MILL
| 0.116-0.125 | 0.166-0.175 | 10: NOMINAL WALL: |  |  | 0.165 | 0.182 | AVG. THICKNESS |  |  | PROJECTED TUBE WALL THICKNESS - 5 YEARS
| 0.126-0.135 | 0.176-0.185 | 10: ASME MIN: |  |  | 0.075 | 0.173 | MIN. THICKNESS |  |  | NO. 1 RECOVERY BOILER
| 0.136-0.145 | 0.186-0.999 | 10: MILL FLAG: |  |  | 0.115 | 0.0047832 | STD DEV. | Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  | 10 SOOTBLOWER PASS A1
PROJECTION
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Retirement
2025 | [26 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. | [24 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
A | REAR SIDE | Year | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| IK #22 C/L |  | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
| 0' REFERENCE |  | May 2055 | ND | ND | ND | ND | ND | ND | ND | May 2055 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| PROJECTED TO REACH TMIN: |  | 10: NOTE: CORROSION RATE IS BASED ON COMPARISON OF | EARLIEST DATE OF PROJECTED RETIREMENT: |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | INTERNATIONAL PAPER
LEGEND | + 5 YEARS (or no data) | [24 empty] | RIVERDALE MILL
| WITHIN 5 YEARS |  | 10: 2020, 2023, 2024, 2025 |  |  |  | PROJECTED TUBE RETIREMENT DATE
| WITHIN 3 YEARS |  | 10: INSPECTION DATA | May 2055 |  |  | NO. 1 RECOVERY BOILER
| WITHIN 1 YEAR |  | 10: ND; 15: NO COMPARISON DATA |  | Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  | 10 SOOTBLOWER PASS A1
RETIREMENT
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com

## Low (hidden)
2025 | [30 empty] | OBSTRUCTION
|  | TUBES NUMBERED LEFT TO RIGHT FACING WALL. LOW THICKNESS MEASUREMENTS ARE IN INCHES. | [28 empty] | ORIENTATION
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | REAR SIDE | LOWEST | 1: 0.176; 2: 0.18; 3: 0.188; 6: 0.183; 9: 0.179; 12: 0.184; 15: 0.181; 18: 0.178; 19: 0.186; 20: 0.184 | 0.1819 | 0.176
0.075 | IK #22 C/L | [21 empty] | 10.5 | 1
| 0' REFERENCE | [21 empty] | 10.5 | 1
ELEVATION |  | LOC | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | AVG | MIN
A | 0.001-0.075 | 0.146-0.155 | 10: OUTSIDE DIAMETER: |  |  | 2.5 | INSPECTION RESULTS |  |  | APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com | INTERNATIONAL PAPER
LEGEND | 0.076-0.115 | 0.156-0.165 | 10: TUBE MATERIAL: |  |  | SA-213T22 | 0.188 | MAX. THICKNESS |  |  | RIVERDALE MILL
| 0.116-0.125 | 0.166-0.175 | 10: NOMINAL WALL: |  |  | 0.165 | 0.181 | AVG. THICKNESS |  |  | TUBE WALL THICKNESS SURVEY (LOW VALUE)
| 0.126-0.135 | 0.176-0.185 | 10: ASME MIN: |  |  | 0.075 | 0.176 | MIN. THICKNESS |  |  | NO. 1 RECOVERY BOILER
| 0.136-0.145 | 0.186-0.999 | 10: MILL FLAG: |  |  | 0.115 | 0.003755 | STD DEV. | Job # H449364 P.O. # 0018342455 W.O. # N/A Date: 5/05/2025 |  | 10 SOOTBLOWER PASS A1
LOW THICKNESS
APPLIED TECHNICAL SERVICES 1049 Triad Court Marietta, Georgia 30062 Office # (770) 423-1400 Fax # (770) 514-3299 www.atslab.com
APPLIED TECHNICAL SERVICES 1325-B Cavalier Boulevard Chesapeake, Virginia 23323 (757) 558-0016 Fax (757) 558-0063 www.atslab.com
APPLIED TECHNICAL SERVICES 2312 Commerce Ctr. Dr., Suite A Rockville, Virginia 23146 (804) 550-7610 Fax (804) 550-7611 www.atslab.com